## IS 15683
IS 15683:2018 INTERNAL TEST RECORDS
Doc No.: F/QAC/R/046 Rev. 00 Date:
MFG Month | Date | ItemCode | Qty | SrNoRange | BatchNo | Cl. 5.3.1 | Cl. 5.3.2 | Cl. 7.2 |  | Cl. 7.4.1 | Cl. 9.3 | Cl. 9.4
[6 empty] | Fill density | Filling tolerance | Min. Duration (in Sec) | Range | Partial discharge | Carrying Handle | Wall Mounting
[6 empty] | CO2- 0.667 CA- 1.19 | CO2/WM/CA/F/W- +5% Powder- ±2% | 1A- 8 Sec, 2A+- 13 8B to 34B- 8 55 to 89B- 9 144 to 233B- 15 | Min. 2 meter | 2nd Pressure / Weight not less than 75% of first | Clearance-25 mm L- min. 75/90 mm | Horizontal & Verticle Motion Min. 6 mm Withstand Load 5 times the mass
[6 empty] | 1 Sample | 1 Sample | 1 Sample |  | 1 Sample | All | 2 Samples
[Data]
[Data]

## IS 16018
IS 16018:2012 INTERNAL TEST RECORDS
Doc No.: F/QAC/R/047 Rev. 00 Date:
MFG Month | Date | ItemCode | Qty | SrNoRange | BatchNo | Cl. 5.3 | Cl. 5.4 | Cl. 6.4 | 6.5 | Cl. 8.6 | Cl. 8.8.2 | Cl. 8.11 | Cl. 8.13 | Cl. 8.14 | Cl. 8.15 | Cl. 8.18
[6 empty] | Fill density | Filling tolerance | Retention of charge | Intermittent discharge | Wall thickness | Anti overfill (for Water based) | Discharge Assembly | Discharge Horn test | Method of operation | Safety Locking device | Carriage Assembly
[6 empty] | CO2- 0.667 CA- 1.19 | CO2/WM/CA/F/W- +5% Powder- ±2% | Pressure loss not more than 10% of Service pressure | Min. 90% to discharge | Min - 3 mm (25 kg), Min. 4 mm (50+ kg) | Liquid level Indicator for water based
[6 empty] | 1/batch | 1/batch | 1/Every 7th batch | 1/Every 7th batch | All | 2/batch | 1/Every 7th batch | 1/Every 7th batch | 1/Every 10th batch | 1/Every 10th batch | 1/batch
[Data]
.