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ANNEXURE-[[H01]]
Test Report No.: PRT/16018/BC/ [[TCNo]] 				       					Date: [[TCDate]]

Performance Requirement Test as per Clause 6.2. 
	
Requirement:
· Effective Discharge time: The effective discharge time of wheeled fire extinguishers shall not be less than 30 s except CO2 Fire extinguisher for which it shall not be less than 15 s.

· Bulk Range: The bulk range throw of wheeled fire extinguishers with ‘Class A’ rating shall be not less than 6 m when tested as follows.
Procedure: 
· Condition the extinguisher for not less than 18 h at a temperature of 27±5 °C and place it in its normal operating position with the discharge nozzle held horizontally at a height of 1 m.
· Fully discharge the extinguisher with the control valve fully open within 5 min of conditioning.
· Record the bulk range throw at the time corresponding to 50 percent of the effective discharge time.

Observations	
	[[ProductDesc]]

	

	Cylinder Sr. Nos.
	Capacity
	Discharge Time
	Bulk Range
	Remarks

	
	
	Required
	Observed
	Required
	Observed
	

	[[SrNo1_1]]
	25 Kg
	30 sec.
	[[R]:R42-45] sec
	6 m
	[[R]:R7-8] m
	Pass

	[[SrNo2_1]] 
	50 Kg
	30 sec.
	[[R]:R51-54] sec
	6 m
	[[R]:R7-8] m
	Pass

	[[SrNo3_1]]
	75 Kg
	30 sec.
	[[R]:R55-57] sec
	6 m
	[[R]:R7-8] m
	Pass
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