ANNEXURE-[[H01]]

Test Report No.: PRT/16018/BC/ [[TCNo]] 				       					Date: [[TCDate]]

Performance Requirement Test as per Clause 6.2.

Requirement:

- Effective Discharge time: The effective discharge time of wheeled fire extinguishers shall not be less than 30 s except CO2 Fire extinguisher for which it shall not be less than 15 s.

- Bulk Range: The bulk range throw of wheeled fire extinguishers with ‘Class A’ rating shall be not less than 6 m when tested as follows.

Procedure:

- Condition the extinguisher for not less than 18 h at a temperature of 27±5 °C and place it in its normal operating position with the discharge nozzle held horizontally at a height of 1 m.

- Fully discharge the extinguisher with the control valve fully open within 5 min of conditioning.

- Record the bulk range throw at the time corresponding to 50 percent of the effective discharge time.

Observations

| [[ProductDesc]] |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Cylinder Sr. Nos. | Capacity | Discharge Time |  | Bulk Range |  | Remarks |
|  |  | Required | Observed | Required | Observed |  |
| [[SrNo1_1]] | 25 Kg | 30 sec. | [[R]:R42-45] sec | 6 m | [[R]:R7-8] m | Pass |
| [[SrNo2_1]] | 50 Kg | 30 sec. | [[R]:R51-54] sec | 6 m | [[R]:R7-8] m | Pass |
| [[SrNo3_1]] | 75 Kg | 30 sec. | [[R]:R55-57] sec | 6 m | [[R]:R7-8] m | Pass |