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ANNEXURE-B
Test Report No.: RTC/16018/BC/ [[TCNo]]      									Date: [[TCDate]]	
Resistance to temperature change test as per Clause 6.3. 
 Procedure:


Wheeled fire extinguishers shall be able to operate at temperatures between the minimum marked on the extinguisher and + 55°C.
Subject two extinguishers to the temperature cycles as below, one extinguisher to each cycle. Operate the extinguisher with the control valve fully open within 5 min of its removal from the conditioning chamber. If it is not possible to operate the extinguisher within 5 min after its removal from the conditioning chamber, suitable means, such as insulation, shall be used to maintain the extinguisher at the conditioning temperature until discharge.

CYCLE 1								        CYCLE 2
	 [[ProductDesc]]
	
	[[ProductDesc]] 

	Sr. No.
	 Capacity 
	Cylinder Sr. Nos.
	 
	Sr. No.
	Capacity
	Cylinder Sr. Nos.

	1
	[[Cap1]]
	[[SrNo1_2]]
	
	4
	[[Cap1]]
	[[SrNo1_3]]

	2
	[[Cap2]]
	[[SrNo2_2]]
	
	5
	[[Cap2]]
	[[SrNo2_3]]

	3
	[[Cap3]]
	[[SrNo3_2]]
	
	6
	[[Cap3]]
	[[SrNo3_3]]



[bookmark: _GoBack]Conditioning:


	Store Temperature
	Duration 
	Start Time
	End Time 
	
	Store Temperature
	Duration 
	Start Time
	End Time

	At Minimum Temp.
 ( -30 °C) +0/-2°C
	24 ± 1 h
	[[TCDate_M3]]
	[[TCDate_M2]]
	
	At  55 ± 5 °C
	24 ± 1 h
	[[TCDate_M3]]
	[[TCDate_M2]]

	
	
	9.30 am
	9.35 am
	
	
	
	9.30 am
	9.35 am

	At  27 ± 2 °C
	24 ± 1 h
	[[TCDate_M2]]
	[[TCDate_M1]]
	
	At  27 ± 2 °C
	24 ± 1 h
	[[TCDate_M2]]
	[[TCDate_M1]]

	
	
	9:35 am
	9:40 am
	
	
	
	9:35 am
	9:40 am

	At  55 ± 5 °C
	24 ± 1 h
	[[TCDate_M1]]
	[[TCDate]]
	
	At Minimum Temp.
 ( -30 °C) +0/-2°C
	24 ± 1 h
	[[TCDate_M1]]
	[[TCDate]]

	
	
	9:40 am
	9:45 am
	
	
	
	9:40 am
	9:45 am



Observations: 

After conditioning the fire extinguishers, the following observations shall be noted:






	Sr. Nos.
	Requirements
	Cycle 1
	 
	Cycle 2

	
	
	[[Cap1]]
	[[Cap2]]
	[[Cap3]]
	[[Cap1]]
	[[Cap2]]
	[[Cap3]]

	1
	Extinguisher shall operate as intended
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory

	2
	Discharge shall commence within 5 s of the opening of the control valve.
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory
	Found Satisfactory

	3
	Not more than 10 percent of the initial charge of medium shall remain within the extinguisher after complete discharge.
	[[R]:R2-3] % 
Found Satisfactory
	[[R]:R1-2] % 
Found Satisfactory
	[[R]:R2-3] % 
Found Satisfactory
	[[R]:R2-3] %
 Found Satisfactory
	[[R]:R1-2] %
 Found Satisfactory
	[[R]:R1-2] % 
Found Satisfactory
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