ANNEXURE-B

Test Report No.: RTC/16018/BC/ [[TCNo]]      									Date: [[TCDate]]

Resistance to temperature change test as per Clause 6.3.

Procedure:

Wheeled fire extinguishers shall be able to operate at temperatures between the minimum marked on the extinguisher and + 55°C.

Subject two extinguishers to the temperature cycles as below, one extinguisher to each cycle. Operate the extinguisher with the control valve fully open within 5 min of its removal from the conditioning chamber. If it is not possible to operate the extinguisher within 5 min after its removal from the conditioning chamber, suitable means, such as insulation, shall be used to maintain the extinguisher at the conditioning temperature until discharge.

CYCLE 1								        CYCLE 2

| [[ProductDesc]] |  |  |  | [[ProductDesc]] |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Sr. No. | Capacity | Cylinder Sr. Nos. |  | Sr. No. | Capacity | Cylinder Sr. Nos. |
| 1 | [[Cap1]] | [[SrNo1_2]] |  | 4 | [[Cap1]] | [[SrNo1_3]] |
| 2 | [[Cap2]] | [[SrNo2_2]] |  | 5 | [[Cap2]] | [[SrNo2_3]] |
| 3 | [[Cap3]] | [[SrNo3_2]] |  | 6 | [[Cap3]] | [[SrNo3_3]] |

Conditioning:

| Store Temperature | Duration | Start Time | End Time |  | Store Temperature | Duration | Start Time | End Time |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| At Minimum Temp. ( -30 °C) +0/-2°C | 24 ± 1 h | [[TCDate_M3]] | [[TCDate_M2]] |  | At 55 ± 5 °C | 24 ± 1 h | [[TCDate_M3]] | [[TCDate_M2]] |
|  |  | 9.30 am | 9.35 am |  |  |  | 9.30 am | 9.35 am |
| At 27 ± 2 °C | 24 ± 1 h | [[TCDate_M2]] | [[TCDate_M1]] |  | At 27 ± 2 °C | 24 ± 1 h | [[TCDate_M2]] | [[TCDate_M1]] |
|  |  | 9:35 am | 9:40 am |  |  |  | 9:35 am | 9:40 am |
| At 55 ± 5 °C | 24 ± 1 h | [[TCDate_M1]] | [[TCDate]] |  | At Minimum Temp. ( -30 °C) +0/-2°C | 24 ± 1 h | [[TCDate_M1]] | [[TCDate]] |
|  |  | 9:40 am | 9:45 am |  |  |  | 9:40 am | 9:45 am |

Observations:

After conditioning the fire extinguishers, the following observations shall be noted:

| Sr. Nos. | Requirements | Cycle 1 |  |  | Cycle 2 |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | [[Cap1]] | [[Cap2]] | [[Cap3]] | [[Cap1]] | [[Cap2]] | [[Cap3]] |
| 1 | Extinguisher shall operate as intended | Found Satisfactory | Found Satisfactory | Found Satisfactory | Found Satisfactory | Found Satisfactory | Found Satisfactory |
| 2 | Discharge shall commence within 5 s of the opening of the control valve. | Found Satisfactory | Found Satisfactory | Found Satisfactory | Found Satisfactory | Found Satisfactory | Found Satisfactory |
| 3 | Not more than 10 percent of the initial charge of medium shall remain within the extinguisher after complete discharge. | [[R]:R2-3] % Found Satisfactory | [[R]:R1-2] % Found Satisfactory | [[R]:R2-3] % Found Satisfactory | [[R]:R2-3] % Found Satisfactory | [[R]:R1-2] % Found Satisfactory | [[R]:R1-2] % Found Satisfactory |