ANNEXURE-[[M01]]

Resistance to Temperature Changes as per Clause 7.3

Test Report No.: RTC/ [[TCNo]]      											Date: [[TCDate]]

Test Method:

Subject 2 extinguishers to the temperature cycles given in Table 2, one extinguisher to each cycle.

Operate the extinguisher within 5 min of its removal from the conditioning chamber.

The extinguisher is to be held in normal working position and shall remain immobile for the operation of test.

Note: For cartridge operated extinguishers, the cartridge shall be pierced and the pressure allowed building for 6 sec before opening the control valve.

Test requirements: after having subjected into temperature resistance test the extinguishers shall comply below requirements.

- Shall operate as intended.

- Commence discharging within 5 seconds of opening of the control valve.

- Following cycle 1, Retention of initial charge shall be max 15%.

- Following cycle 2, Retention of initial charge shall be max 20%.

CYCLE 1								                    CYCLE 2

| Sr. No. | Capacity | Cylinder Sr. Nos. |  | Sr. No. | Capacity | Cylinder Sr. Nos. |
| --- | --- | --- | --- | --- | --- | --- |
| [[ProductDesc]] |  |  |  | [[ProductDesc]] |  |  |
| 01 | [[Cap1]] | [[SrNo1_1]] |  | 01 | [[Cap1]] | [[SrNo1_2]] |
| 02 | [[Cap2]] | [[SrNo2_1]] |  | 02 | [[Cap2]] | [[SrNo2_2]] |
| 03 | [[Cap3]] | [[SrNo3_1]] |  | 03 | [[Cap3]] | [[SrNo3_2]] |
| 04 | [[Cap4]] | [[SrNo4_1]] |  | 04 | [[Cap4]] | [[SrNo4_2]] |
| 05 | [[Cap5]] | [[SrNo5_1]] |  | 05 | [[Cap5]] | [[SrNo5_2]] |

Conditioning:

| Sr. No. | Store Temperature | Duration | Start Time | End Time |  | Sr. No. | Store Temperature | Duration | Start Time | End Time |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 01 | @Min. temp. -30°C | 24 ± 1 h | [[TCDate_M3]] | [[TCDate_M2]] |  | 01 | At 60 ± 5 °C | 24 ± 1 h | [[TCDate_M3]] | [[TCDate_M2]] |
|  |  |  | 9:15 AM | 9:25 AM |  |  |  |  | 9:15 AM | 9:25 AM |
| 02 | At 27 ± 5 °C | 24 ± 1 h | [[TCDate_M2]] | [[TCDate_M1]] |  | 02 | At 27 ± 5 °C | 24 ± 1 h | [[TCDate_M2]] | [[TCDate_M1]] |
|  |  |  | 9:25 AM | 9:35 AM |  |  |  |  | 9:25 AM | 9:35 AM |
| 03 | At 60 ± 5 °C | 24 ± 1 h | [[TCDate_M1]] | [[TCDate]] |  | 03 | At min. temp. -30 °C | 24 ± 1 h | [[TCDate_M1]] | [[TCDate]] |
|  |  |  | 9:35 AM | 9:45 AM |  |  |  |  | 9:35 AM | 9:45 AM |

Observations:

| Sr. No. | Fire Extinguisher Sr. Nos. | Performance Results |  |  |  |  |  |  |  | Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Discharge Time |  |  | Throw of jet |  |  | Percentage Discharge |  |  |
|  |  | Required |  | observed | Required | observed |  | Required | observed |  |
| CYCLE-1 |  |  |  |  |  |  |  |  |  |  |
| 01 | [[SrNo1_1]] | 8 sec. |  | [[R]:R10-12] sec | 2 m. | [[R]:R2-3] m. | 85% |  | [[R]:P90-96] % | Pass |
| 02 | [[SrNo2_1]] | 8 sec. |  | [[R]:R13-17] sec | 2 m. | [[R]:R3-4] m. | 85% |  | [[R]:P90-96] % | Pass |
| 03 | [[SrNo3_1]] | 13 sec. |  | [[R]:R22-25] sec | 2 m. | [[R]:R4-5] m. | 85% |  | [[R]:P90-97] % | Pass |
| 04 | [[SrNo4_1]] | 15 sec. |  | [[R]:R25-29] sec | 2 m. | [[R]:R5-6] m. | 85% |  | [[R]:P90-99] % | Pass |
| 05 | [[SrNo5_1]] | 15 sec. |  | [[R]:R29-31] sec | 2 m. | [[R]:R5-8] m. | 85% |  | [[R]:P90-100] % | Pass |
| CYCLE-2 |  |  |  |  |  |  |  |  |  |  |
| 01 | [[SrNo1_2]] |  | 8 sec. | [[R]:R10-14] sec. | 2 m. | [[R]:R2-3] m. |  | 80% | [[R]:P90-95] % | Pass |
| 02 | [[SrNo2_2]] |  | 8 sec. | [[R]:R14-22] sec. | 2 m. | [[R]:R3-4] m. |  | 80% | [[R]:P90-94] % | Pass |
| 03 | [[SrNo3_2]] |  | 13 sec. | [[R]:R22-24] sec. | 2 m. | [[R]:R4-5] m. |  | 80% | [[R]:P90-97] % | Pass |
| 04 | [[SrNo4_2]] |  | 15 sec. | [[R]:R24-30] sec. | 2 m. | [[R]:R5-6] m. |  | 80% | [[R]:P90-98] % | Pass |
| 05 | [[SrNo5_2]] |  | 15 sec. | [[R]:R30-32] sec. | 2 m. | [[R]:R5-8] m. |  | 80% | [[R]:P90-100] % | Pass |