Test Report No.: RIT/ [[TCNo]]	                           					Date: [[TCDate]]

ANNEXURE [[M02]]

Resistance to Impact Test as per Clause 7.5.1

Test Method:

Condition the fully charged extinguisher with all the fittings at -30⁰C (±5⁰C) working temperature for 18 hr, within 5 min after removal of extinguisher from conditioning chamber subject it to test as  below,

Drop the cylindrical hammer with Diameter 75 mm. & total mass 4.0 kg freely through a height of min. 300 mm. or given by,

h=M/20 (h-height, expressed in m; M- total mass of extinguisher in kg.)

The extinguisher shall be placed on a rigid flat surface protecting pressure gauge in each of the following positions

- In the normal Up-Right position with longitudinal axis of the hammer coincident with longitudinal axis of valve and

- Lying on its side so that the valve rests on a rigid fixed steel block.

Note: If the extinguisher is of the gas cartridge type, activate the extinguisher before testing.

Requirements:

The extinguisher shall not release pressure in a potentially dangerous manner, when a cylindrical hammer of 4 kg is dropped on valve head in both upright position & horizontally lying position, point of impact to be examined.

| [[ProductDesc]] |  | [[Cap1]] |  | [[Cap2]] | [[Cap3]] |  | [[Cap4]] | [[Cap5]] |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Cylinder Sr. Nos. |  | [[SrNo1_3]] |  | [[SrNo2_3]] | [[SrNo3_3]] |  | [[SrNo4_3]] | [[SrNo5_3]] |
| Observations |  |  |  |  |  |  |  |  |  |  |  |  |
| Sr. No. | Particulars |  | Requirements |  |  | Remarks |  |  |
| 01 | Test on Fire extinguisher Up-Right position |  | The pressure shall not be released in a potentially dangerous manner |  |  | No pressure released in all above cases and found satisfactory |  |  |
| 02 | Test on Fire extinguisher lying horizontal |  | The pressure shall not be released in a potentially dangerous manner |  |  | No pressure released in all above cases and found satisfactory |  |  |