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ANNEXURE [[M03]]

Resistance to Vibration test as per Clause 7.5.2  

Test Method:

Axes of orientation:

Subject the extinguisher to the vibration test in horizontal & vertical axes for the below parameters

Vibration parameters: 
Frequency: 40 Hz, Amplitude: 0.5 mm Min.  Duration: 2 h (in each orientation)

Test Requirements:

Following Exposure to the vibration test,
a) The extinguisher shall comply with the discharge requirements specified in 7.2 
b) Physical failure of components which require repair or replacement of the extinguisher and/or components before it can be returned to normal service shall be cause of rejection.

	[[ProductDesc]]
	[[Cap1]] 
	[[Cap2]] 
	[[Cap3]] 
	[[Cap4]] 
	[[Cap5]] 

	Cylinder Sr. Nos.
	[[SrNo1_4]]
	[[SrNo2_4]]
	[[SrNo3_4]]
	[[SrNo4_4]]
	[[SrNo5_4]]



  Observations:

	Cylinder Sr. Nos.
	Min. discharge time
	Min. Throw
	% Discharge
	Remarks

	
	Requirement
	Result
	Requirement
	Result
	Requirement
	Result
	

	[[SrNo1_4]]
	8 sec.
	[[R]:R10-15] sec.
	2 m.
	[[R]:R3-5] m.
	85%
	[[R]:P90-100] %
	Pass

	[[SrNo2_4]]
	8 sec.
	[[R]:R10-15] sec.
	2 m.
	[[R]:R3-5]  m.
	85%
	[[R]:P90-100]  %
	Pass

	[[SrNo3_4]]
	13 sec.
	[[R]:R22-25] sec.
	2 m.
	[[R]:R3-5]  m.
	85%
	[[R]:P90-100]  %
	Pass

	[[SrNo4_4]]
	15 sec.
	[[R]:R25-28] sec.
	2 m.
	[[R]:R5-6]  m.
	85%
	[[R]:P90-100]  %
	Pass

	[[SrNo5_4]]
	15 sec.
	[[R]:R28-30] sec.
	2 m.
	[[R]:R6-7]  m.
	85%
	[[R]:P90-100]  %
	Pass
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