Test Report No.: ECT/ [[TCNo]]	           						Date: [[TCDate2]]

ANNEXURE-[[M04]]

Resistance to Corrosion (External) test as per Clause 7.6.1

Sample Quantity: One sample from the same family

Test method:

- Test Solution for salt spray be prepared by dissolving 50±5 g of sodium chloride per liter of water

- Subject fully charged extinguishers, including mounting bracket and wall hook to a salt spray test   for a period of 240 h.

- Drying period of at least 24 h at room temperature

- Carefully wash the extinguisher to remove any salt deposits

| [[ProductDesc]] | [[Cap1]] | [[Cap2]] | [[Cap3]] | [[Cap4]] | [[Cap5]] |
| --- | --- | --- | --- | --- | --- |
| Cylinder Sr. Nos. | [[SrNo1_5]] | [[SrNo2_5]] | [[SrNo3_5]] | [[SrNo4_5]] | [[SrNo5_5]] |

Observations:

| Requirement | Observations |
| --- | --- |
| - The mechanical operation of all working parts shall be unimpaired. | Complied |
| - The minimum effective discharge time and method operation shall comply with requirement. | Complied |
| - The Pressure gauge, if one is fitted, shall remain functional and watertight. | No corrosion |
| - There shall be no corrosion of the metal of the extinguisher body, discoloration/superficial corrosion of non ferrous metals is acceptable but galvanic corrosion between dissimilar metals shall not be permitted. | No discoloration/ Superficial corrosion found |

| Sr. No. | Min. discharge time |  | Method of operation | Remarks |
| --- | --- | --- | --- | --- |
|  | Requirement | Result |  |  |
| [[SrNo1_5]] | 8 sec. | [[R]:R10-15] sec. | Complied | Pass |
| [[SrNo2_5]] | 8 sec. | [[R]:R10-15] sec. | Complied | Pass |
| [[SrNo3_5]] | 13 sec. | [[R]:R22-24] Sec. | Complied | Pass |
| [[SrNo4_5]] | 15 sec. | [[R]:R24-27] sec. | Complied | Pass |
| [[SrNo5_5]] | 15 sec. | [[R]:R29-31] sec. | Complied | Pass |