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ANNEXURE-[[M04]]

Resistance to Corrosion (External) test as per Clause 7.6.1  
	
Sample Quantity: One sample from the same family

Test method:
· Test Solution for salt spray be prepared by dissolving 50±5 g of sodium chloride per liter of water
· Subject fully charged extinguishers, including mounting bracket and wall hook to a salt spray test   for a period of 240 h.
· Drying period of at least 24 h at room temperature
· Carefully wash the extinguisher to remove any salt deposits

	[[ProductDesc]]
	[[Cap1]] 
	[[Cap2]]
	[[Cap3]]
	[[Cap4]]
	[[Cap5]]

	Cylinder Sr. Nos.
	[[SrNo1_5]]
	[[SrNo2_5]]
	[[SrNo3_5]]
	[[SrNo4_5]]
	[[SrNo5_5]]



Observations:
	Requirement 
	Observations

	a. The mechanical operation of all working parts shall be unimpaired.   
	Complied

	b. The minimum effective discharge time and method operation shall comply with requirement. 
	Complied

	c. The Pressure gauge, if one is fitted, shall remain functional and watertight.  
	No corrosion

	d. There shall be no corrosion of the metal of the extinguisher body, discoloration/superficial corrosion of non ferrous metals is acceptable but galvanic corrosion between dissimilar metals shall not be permitted.
	No discoloration/ Superficial corrosion found



	Sr. No.
	Min. discharge time
	Method of operation
	Remarks

	
	Requirement
	Result
	
	

	[[SrNo1_5]]
	8 sec.
	[[R]:R10-15] sec.
	Complied
	Pass

	[[SrNo2_5]]
	8 sec.
	[[R]:R10-15] sec.
	Complied
	Pass

	[[SrNo3_5]]
	13 sec.
	[[R]:R22-24] Sec.
	Complied
	Pass

	[[SrNo4_5]]
	15 sec.
	[[R]:R24-27] sec.
	Complied
	Pass

	[[SrNo5_5]]
	15 sec.
	[[R]:R29-31] sec.
	Complied
	Pass
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