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ANNEXURE-[[M05]]
Tapping Test as per Clause 7.7  

Test Method:

Normally charged extinguisher held in vertical position and dropped vertical 500 times from a height of 15 mm at a frequency of 1 Hz onto a rigid horizontal steel plate.
The extinguisher is to be removed from the test apparatus with a minimum amount of agitation, held in its normal working position and operated.

Note: for Cartridge extinguishers, pressure of cartridge is allowed to build for 6s after piercing before opening the control valve.

Test parameters: 
· Frequency: 1 Hz, Height of dropping: 20mm, No. of dropping: 500 times
· Commence discharge within 5 s of the opening of the control valve
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Observations:

	Cylinders 
Sr. No.
	Retain percentage
	Remarks

	
	Requirement
	Observation
	

	[[SrNo1_6]]
	Not more than 15% 
	[[R]:R5-6] %
	Pass

	              [[SrNo2_6]]
	
	[[R]:R5-6] %
	Pass

	[[SrNo3_6]]
	
	[[R]:R5-6] %
	Pass

	              [[SrNo4_6]]
	
	               [[R]:R5-6] %
	Pass

	              [[SrNo5_6]]
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	Pass
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