Test Report No.: INT/ [[TCNo]]		           						Date: [[TCDate2]]

ANNEXURE-[[M06]]

Intermittent Discharge test Clause 7.8

Test Method:

Operate the extinguisher intermittently by opening and closing the valve in cycles of 2s open 2 s closed until the end of discharge is reached.

Note: For cartridge operated extinguishers, pierce the cartridge and allow the pressure to build for 6 s before opening the control valve.

Test requirement:

At the end of discharge test, the extinguishers shall not retain,

- Powder : 15 percent

- All other : 10 percent

Test procedure:

Condition the fully charged extinguishers at 27±5⁰C and 60±5⁰C, each at minimum 18 hr.

| [[ProductDesc]] | [[Cap1]] | [[Cap2]] | [[Cap3]] | [[Cap4]] | [[Cap5]] |
| --- | --- | --- | --- | --- | --- |
| Cylinder Sr. Nos. | [[SrNo1_7]] | [[SrNo2_7]] | [[SrNo3_7]] | [[SrNo4_7]] | [[SrNo5_7]] |

| Store Temperature | Duration | Start Time | End Time |
| --- | --- | --- | --- |
| 27 ± 5°C | 18 h | 10:30 AM | 04:30 PM |
| 60 ± 5°C | 18 h | 04:30 PM | 10:30 AM |

Observations:

| Cylinders Sr. No. | Retain percentage |  | Remarks |
| --- | --- | --- | --- |
|  | Requirement | Observation |  |
| [[SrNo1_7]] | Powder: Not more than 15% All other: Not more than 10% | [[R]:R5-6] % | Pass |
| [[SrNo2_7]] |  | [[R]:R5-6] % | Pass |
| [[SrNo3_7]] |  | [[R]:R5-6] % | Pass |
| [[SrNo4_7]] |  | [[R]:R4-6] % | Pass |
| [[SrNo5_7]] |  | [[R]:R5-6] % | Pass |