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Internal Corrosion test for Extinguishers Clause 7.6.2
     
		 
Test method:

Condition the extinguisher at an elevated temperature of 60± 5°C for 7 days in an oven, then bring back to 27 ± 5 °C for 24 hours and there after discharge the Extinguisher and then cut it to examine.

Test Requirement:

There shall be no visible signs of corrosion of the metal or detachment, cracking or bubbling. There shall be no visible change in the color of the extinguishing medium other than that resulting from thermal cycling in case of water based extinguishers.

	Type and Capacity of Fire extinguisher
	Cylinder Sr. Nos.
	Date and time of Conditioning

	[[ProductDesc]]
	[[SrNo1_11]]
	 [[TCDate_M3]]   9:30 AM


                                                                                  
Observations:

	Requirements
	Remarks

	No visible signs of corrosion of the metal or detachment, cracking or bubbling
	

	There shall be no visible change in the color of the extinguishing medium other than that resulting from thermal cycling in case of water based extinguishers
	



                                                                                                 
QC Assistant		                                           QC In charge
