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Horn test for Carbon Di Oxide Extinguishers Clause 9.13




Test method and requirement:

The Extinguisher Horn shall be constructed to withstand crushing when 25 kg is applied to its extremity for 5 min immediately after having completely discharged the extinguisher through the horn.

a. Condition the horn at 55°C for 18 hrs.
b. Attach the horn to a fully charged extinguisher.
c. Discharge the extinguisher with the valve fully open.
d. Subject the horn to a static load of 25 kg using a circular contact surface of 50 mm diameter for 5 min. applied at the end of the horn.
e. Check that the horn doesn’t show any evidence of cracking or breakage.

Observations:

No cracking and breakage of the horn found hence passes the test.
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