Test Report No.: HRNT/ [[TCNo]]		       					Date: [[TCDate3]]

ANNEXURE-[[M11]]

Horn test for Carbon Di Oxide Extinguishers Clause 9.13

Test method and requirement:

The Extinguisher Horn shall be constructed to withstand crushing when 25 kg is applied to its extremity for 5 min immediately after having completely discharged the extinguisher through the horn.

- Condition the horn at 55°C for 18 hrs.

- Attach the horn to a fully charged extinguisher.

- Discharge the extinguisher with the valve fully open.

- Subject the horn to a static load of 25 kg using a circular contact surface of 50 mm diameter for 5 min. applied at the end of the horn.

- Check that the horn doesn’t show any evidence of cracking or breakage.

Observations:

No cracking and breakage of the horn found hence passes the test.