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ANNEXURE-[[M15]]
Class ‘F’ Splash Test Fire Clause 8.7 

Test Method:

Operate the conditioned extinguishers towards the center of the tray which is covered with a layer of sodium bicarbonate not more than 2 mm deep.


Test requirement:

The discharge from the extinguishers when tested in accordance with Cl 8.7.1 to 8.7.4 shall not splash grease droplets in excess of 5 mm diameter.

Test procedure:

Condition the fully charged extinguishers at 5⁰C and 60⁰C, each at minimum 18 hr.
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	Store Temperature
	Duration
	Start Time
	End Time

	5 °C
	18 h
	10:30  AM
	04:30 AM

	60 °C
	18 h
	04:30  AM
	10:30 AM




Observations:

	[[ProductDesc]]
	[[Cap1]] 
	[[Cap2]]
	[[Cap3]]
	[[Cap4]]
	[[Cap5]]

	Cylinder Sr. No. (5 °C)
	[[SrNo1_15]]
	[[SrNo2_15]]
	[[SrNo3_15]]
	[[SrNo4_15]]
	[[SrNo5_15]]

	Observation
	Pass
	Pass
	Pass
	Pass
	Pass

	Cylinder Sr. No. (60°C)
	[[SrNo1_16]]
	[[SrNo2_16]]
	[[SrNo3_16]]
	[[SrNo4_16]]
	[[SrNo5_16]]

	Observation
	Pass
	Pass
	Pass
	Pass
	Pass
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