Test Report No.: EC/[[TCNo]]		           					Date: [[TCDate3]]

ANNEXURE-[[M16]]

Electrical Conductivity of Extinguisher Discharge Clause 8.8

Test Method:

Connect a metal plate to a transformer so that alternating voltage of 36 ±3.6kV is established between the plate and the earth. Mount the extinguisher on an insulating support with the nozzle/handle fixed 1 m from the center of the plate.

Measure any current flowing between the earth and the extinguisher when the plate is live and the extinguisher discharging.

Requirement:

The current between the handle/nozzle and earth and between the earth and extinguisher shall be no more than 0.5 mA at any time during the complete discharge duration of the extinguisher.

Observations:

| [[ProductDesc]] |  |  |  |
| --- | --- | --- | --- |
| Capacity | Cylinder | Observed Current (mA) | Conclusion |
| [[Cap1]] | [[SrNo1_17]] | [[R]:R0.2-0.3] | PASS |
| [[Cap2]] | [[SrNo1_17]] | [[R]:R0.2-0.3] | PASS |
| [[Cap3]] | [[SrNo1_17]] | [[R]:R0.3-0.4] | PASS |
| [[Cap4]] | [[SrNo1_17]] | [[R]:R0.3-0.4] | PASS |
| [[Cap5]] | [[SrNo1_17]] | [[R]:R0.3-0.4] | PASS |